# Site Geometry and Coordinate Report

DRAFT - AI-assisted engineering output. Requires human engineering review and approval before issue. CONCEPTUAL - NOT FOR CONSTRUCTION.

| Document no. | Revision | Date | Workstream | Status | Project |
| --- | --- | --- | --- | --- | --- |
| HAS-SAH-2026-WS3-D14-RevA | A | 2026-10-13 | WS3 - PV and Balance of Plant Engineering | DRAFT | Solara Alentejo Hybrid (PV + BESS) |

# 1. Purpose and scope

This deliverable ('Site Geometry and Coordinate Report') is generated from the project blackboard for Solara Alentejo Hybrid (PV + BESS). It reports evidence-backed findings and deterministic calculation results; it does not contain unreferenced engineering conclusions.

| Parameter | Value |
| --- | --- |
| PV DC / AC | 150.0 MWp / 120.0 MWac |
| BESS | 60 MW / 270.0 MWh DC (240 MWh usable at POI) |
| Export limit | 130 MW |
| Location | 37.62, -8.19 |

# 2. Basis and assumptions

| ID | Agent | Assumption | Basis |
| --- | --- | --- | --- |
| AS-001 | site_geometry_agent | Site boundary assumed as a 262.0 ha rectangle centred on the stated coordinates. | No surveyed boundary supplied |
| AS-002 | pv_layout_agent | Substation and BESS compound located on the east side of the site; PV layout avoids them. | No site plan supplied - conceptual placement |
| AS-003 | pv_layout_agent | Horizontal single-axis tracker, 1P, N-S axis, GCR 0.33, tables of 48 modules, 10 m perimeter setback. | Typical utility-scale design; confirm with EPC |

# 3. Calculations (deterministic, independently re-run by Calculation Validation Agent)

| Calc ID | Tool | Key outputs |
| --- | --- | --- |
| C001 | site_geometry | {'epsg': 32629, 'utm_zone': 29, 'hemisphere': 'N', 'site_centre_utm': [571481.84, 4163963.04], 'area_ha': 262.0, 'boundary_assumed': True, 'utm_roundtrip_error_m': 0.0001} |

# 4. Findings

| ID | Severity | Statement | Evidence | Recommendation | QA |
| --- | --- | --- | --- | --- | --- |
| F-068 | High | PV DC capacity (kWp): documents disagree - values [148442.9, 150002.0] (spread 1.039%). | 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1; 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1; 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1 (part 2); 05_Design/Design_Basis_Report_SAH.pdf ¦ p.1 | Reconcile and confirm the governing value; update the lower-ranked documents/model. | qa_pass |
| F-001 | Medium | Layout is indicative: no surveyed site boundary was supplied. | calc:C001 | Supply surveyed boundary and constraint layers. | qa_pass |
| F-002 | Medium | With 2 x 90 MVA transformers, N-1 loading at peak export is 152.0% (>100%): loss of one unit constrains export. | calc:C007 | Confirm N-1 philosophy with TSO or add transformer capacity / curtailment scheme. | qa_pass |
| F-012 | Medium | Document indicates an open/absent item: "MISSING (planned Q1 2027) BESS VS-5000 ¦" | 06_Equipment/Certificates_Register.xlsx ¦ sheet:Certificates | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-013 | Medium | Document indicates an open/absent item: "In progress Transformer 90 MVA ¦" | 06_Equipment/Certificates_Register.xlsx ¦ sheet:Certificates | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-015 | Medium | Document indicates an open/absent item: "No pile testing was performed in Blocks C and D; a supplementary programme (min." | 04_Technical_Studies/Geotechnical_Investigation_Report_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-019 | Medium | Document indicates an open/absent item: "PFAS: supplier declarations pending for BESS; PV modules declared PFAS-free backsheet (glass-glass)." | 09_Environmental_Social/ESIA_Summary_and_Biodiversity_Baseline_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-020 | Medium | Document indicates an open/absent item: "Lease signed, registration pending (2 plots) Block D (part) ¦" | 01_Corporate_Legal/Land_Lease_and_Easements_Summary_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-021 | Medium | Document indicates an open/absent item: "<b>Option agreement not yet exercised; no signed lease/easement</b>" | 01_Corporate_Legal/Land_Lease_and_Easements_Summary_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-022 | Medium | Document indicates an open/absent item: "A desk-study by a specialist UXO consultant has not been commissioned." | 04_Technical_Studies/UXO_Screening_Note_SAH.pdf ¦ p.1 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-023 | Medium | Document indicates an open/absent item: "Grid-forming functionality: not included in the current scope." | 05_Design/Design_Basis_Report_SAH.pdf ¦ p.2 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |

# 5. Outstanding information (OIRs)

| ID | Question | Reason | Priority | Routed to |
| --- | --- | --- | --- | --- |
| OIR-001 | Provide the surveyed site boundary (KML/GeoJSON/DXF) with CRS. | Layout, area and constraint checks are indicative until a surveyed boundary is available | High | layout_constructability |

# 6. QA status

Independent QA checks for WS3: pass 33, warn 2, fail 1.

| Check | Agent | Status | Detail |
| --- | --- | --- | --- |
| CONTRA-01 | contradiction_detection | fail | PV DC capacity (kWp): values [148442.9, 150002.0] across 3 documents (spread 1.04%) |
| COORD-03 | coordinate_consistency | warn | site boundary was NOT supplied: an assumed rectangle was generated - layout is indicative only; supply surveyed boundary |
| XD-08 | cross_discipline | warn | transformer N-1 loading 152.0% (>100% means one unit cannot carry peak export) |

## Approval record

| Gate | Role | Decision | Actor | Date | Comment |
| --- | --- | --- | --- | --- | --- |
| engineering_review | Engineering Reviewer | PENDING |  |  |  |
| lead_approval | Lead Engineer | PENDING |  |  |  |
| director_approval | Project Director | PENDING |  |  |  |