# Constructability Assessment

DRAFT - AI-assisted engineering output. Requires human engineering review and approval before issue. CONCEPTUAL - NOT FOR CONSTRUCTION.

| Document no. | Revision | Date | Workstream | Status | Project |
| --- | --- | --- | --- | --- | --- |
| HAS-SAH-2026-WS3-D21-RevA | A | 2026-10-13 | WS3 - PV and Balance of Plant Engineering | DRAFT | Solara Alentejo Hybrid (PV + BESS) |

# 1. Purpose and scope

This deliverable ('Constructability Assessment') is generated from the project blackboard for Solara Alentejo Hybrid (PV + BESS). It reports evidence-backed findings and deterministic calculation results; it does not contain unreferenced engineering conclusions.

| Parameter | Value |
| --- | --- |
| PV DC / AC | 150.0 MWp / 120.0 MWac |
| BESS | 60 MW / 270.0 MWh DC (240 MWh usable at POI) |
| Export limit | 130 MW |
| Location | 37.62, -8.19 |

# 2. Basis and assumptions

| ID | Agent | Assumption | Basis |
| --- | --- | --- | --- |
| AS-001 | site_geometry_agent | Site boundary assumed as a 262.0 ha rectangle centred on the stated coordinates. | No surveyed boundary supplied |
| AS-002 | pv_layout_agent | Substation and BESS compound located on the east side of the site; PV layout avoids them. | No site plan supplied - conceptual placement |
| AS-003 | pv_layout_agent | Horizontal single-axis tracker, 1P, N-S axis, GCR 0.33, tables of 48 modules, 10 m perimeter setback. | Typical utility-scale design; confirm with EPC |

# 3. Calculations (deterministic, independently re-run by Calculation Validation Agent)

| Calc ID | Tool | Key outputs |
| --- | --- | --- |
| C002 | pv_layout | {'table_len_m': 54.43, 'table_w_m': 2.278, 'pitch_m': 6.9, 'gcr': 0.33, 'modules_placed': 258621, 'modules_required': 258621, 'kwp_placed': 150000.2, 'kwp_target': 150000.0} |

# 4. Findings

| ID | Severity | Statement | Evidence | Recommendation | QA |
| --- | --- | --- | --- | --- | --- |
| F-001 | Medium | Layout is indicative: no surveyed site boundary was supplied. | calc:C001 | Supply surveyed boundary and constraint layers. | qa_pass |
| F-020 | Medium | Document indicates an open/absent item: "Lease signed, registration pending (2 plots) Block D (part) ¦" | 01_Corporate_Legal/Land_Lease_and_Easements_Summary_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-021 | Medium | Document indicates an open/absent item: "<b>Option agreement not yet exercised; no signed lease/easement</b>" | 01_Corporate_Legal/Land_Lease_and_Easements_Summary_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-022 | Medium | Document indicates an open/absent item: "A desk-study by a specialist UXO consultant has not been commissioned." | 04_Technical_Studies/UXO_Screening_Note_SAH.pdf ¦ p.1 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |

# 5. Outstanding information (OIRs)

| ID | Question | Reason | Priority | Routed to |
| --- | --- | --- | --- | --- |
| OIR-001 | Provide the surveyed site boundary (KML/GeoJSON/DXF) with CRS. | Layout, area and constraint checks are indicative until a surveyed boundary is available | High | layout_constructability |

# 6. QA status

Independent QA checks for WS3: pass 33, warn 2, fail 1.

| Check | Agent | Status | Detail |
| --- | --- | --- | --- |
| CONTRA-01 | contradiction_detection | fail | PV DC capacity (kWp): values [148442.9, 150002.0] across 3 documents (spread 1.04%) |
| COORD-03 | coordinate_consistency | warn | site boundary was NOT supplied: an assumed rectangle was generated - layout is indicative only; supply surveyed boundary |
| XD-08 | cross_discipline | warn | transformer N-1 loading 152.0% (>100% means one unit cannot carry peak export) |

## Approval record

| Gate | Role | Decision | Actor | Date | Comment |
| --- | --- | --- | --- | --- | --- |
| engineering_review | Engineering Reviewer | PENDING |  |  |  |
| lead_approval | Lead Engineer | PENDING |  |  |  |
| director_approval | Project Director | PENDING |  |  |  |