# Grid Connection Compliance Review

DRAFT - AI-assisted engineering output. Requires human engineering review and approval before issue. CONCEPTUAL - NOT FOR CONSTRUCTION.

| Document no. | Revision | Date | Workstream | Status | Project |
| --- | --- | --- | --- | --- | --- |
| HAS-SAH-2026-WS4-D25-RevA | A | 2026-10-13 | WS4 - Grid, Controls and Digital Systems | DRAFT | Solara Alentejo Hybrid (PV + BESS) |

# 1. Purpose and scope

This deliverable ('Grid Connection Compliance Review') is generated from the project blackboard for Solara Alentejo Hybrid (PV + BESS). It reports evidence-backed findings and deterministic calculation results; it does not contain unreferenced engineering conclusions.

| Parameter | Value |
| --- | --- |
| PV DC / AC | 150.0 MWp / 120.0 MWac |
| BESS | 60 MW / 270.0 MWh DC (240 MWh usable at POI) |
| Export limit | 130 MW |
| Location | 37.62, -8.19 |

# 2. Basis and assumptions

| ID | Agent | Assumption | Basis |
| --- | --- | --- | --- |
| AS-001 | site_geometry_agent | Site boundary assumed as a 262.0 ha rectangle centred on the stated coordinates. | No surveyed boundary supplied |
| AS-002 | pv_layout_agent | Substation and BESS compound located on the east side of the site; PV layout avoids them. | No site plan supplied - conceptual placement |
| AS-003 | pv_layout_agent | Horizontal single-axis tracker, 1P, N-S axis, GCR 0.33, tables of 48 modules, 10 m perimeter setback. | Typical utility-scale design; confirm with EPC |

# 4. Findings

| ID | Severity | Statement | Evidence | Recommendation | QA |
| --- | --- | --- | --- | --- | --- |
| F-023 | Medium | Document indicates an open/absent item: "Grid-forming functionality: not included in the current scope." | 05_Design/Design_Basis_Report_SAH.pdf ¦ p.2 | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-030 | Medium | Document indicates an open/absent item: "Open items EMT model validation for the selected PCS has not yet been submitted." | 08_Grid/Grid_Connection_Study_and_TSO_Letter_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-031 | Medium | Document indicates an open/absent item: "Grid-code compliance study (including GFM) not yet issued." | 08_Grid/Grid_Connection_Study_and_TSO_Letter_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. | qa_pass |
| F-003 | Info | PV (120.0 MWac) + BESS (60 MW) exceeds the 130 MW export limit; PPC export limiting is required. | calc:C007 | Quantify curtailment and BESS co-optimisation in the yield/revenue model. | qa_pass |

# 5. Outstanding information (OIRs)

None.

# 6. QA status

Independent QA checks for WS4: pass 17, warn 1, fail 0.

| Check | Agent | Status | Detail |
| --- | --- | --- | --- |
| XD-09 | cross_discipline | warn | PV+BESS nameplate exceeds export limit - PPC limitation must be implemented and revenue impact assessed |

## Approval record

| Gate | Role | Decision | Actor | Date | Comment |
| --- | --- | --- | --- | --- | --- |
| engineering_review | Engineering Reviewer | PENDING |  |  |  |
| lead_approval | Lead Engineer | PENDING |  |  |  |
| director_approval | Project Director | PENDING |  |  |  |