# Lender Technical Due Diligence Report

DRAFT - AI-assisted engineering output. Requires human engineering review and approval before issue. CONCEPTUAL - NOT FOR CONSTRUCTION.

| Document no. | Revision | Date | Workstream | Status | Project |
| --- | --- | --- | --- | --- | --- |
| HAS-SAH-2026-WS8-D49-RevA | A | 2026-10-13 | WS8 - Independent Assurance and Reporting | DRAFT | Solara Alentejo Hybrid (PV + BESS) |

# 1. Scope and method

Lender-grade technical due diligence synthesis: discipline agents, deterministic tools, evidence retrieval, independent QA. All findings are traceable to a data-room citation or a calculation ID.

# 2. Findings summary

| Severity | Count |
| --- | --- |
| Critical | 0 |
| High | 3 |
| Medium | 27 |
| Low | 0 |
| Info | 2 |

## 3.1 WS1 - Project Governance and Requirements

| ID | Sev. | Finding | Evidence | Recommendation | CP |
| --- | --- | --- | --- | --- | --- |
| F-006 | Medium | Document indicates an open/absent item: "(unrated; parent company guarantee of EUR 15 m)." | 07_Contracts/PPA_Key_Terms_SAH.docx ¦ body | Confirm with the project team; request the missing evidence or close-out. |  |
| F-007 | Medium | Document indicates an open/absent item: "PENDING - not yet uploaded DR-P02 ¦" | 00_Index/Data_Room_Index_SAH.xlsx ¦ sheet:Index (part 5) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-008 | Medium | Document indicates an open/absent item: "PENDING - not yet uploaded DR-P03 ¦" | 00_Index/Data_Room_Index_SAH.xlsx ¦ sheet:Index (part 5) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-009 | Medium | Document indicates an open/absent item: "NFPA 855 Annex / CSA C800) Not available for VS-5000; test planned Q1 2027 IEC 62933-5-2 (safety) In progress UN 38.3 Certified" | 06_Equipment/BESS_Container_Datasheet_Voltaris_VS5000.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-010 | Medium | Document indicates an open/absent item: "Seller must curtail when day-ahead price < 0 at Buyer's request without compensation (max 150 h/yr) Termination ¦" | 07_Contracts/PPA_Key_Terms_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. |  |

## 3.2 WS2 - Solar Resource and Energy Yield

| ID | Sev. | Finding | Evidence | Recommendation | CP |
| --- | --- | --- | --- | --- | --- |
| F-069 | High | Annual module degradation (%/yr): documents disagree - values [0.25, 0.4] (spread 37.5%). | 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.2; 06_Equipment/Module_Datasheet_Helion_HX580BF.pdf ¦ p.1; 07_Contracts/Module_Supply_Agreement_Key_Terms_SAH.docx ¦ body; 10_Financial/Financial_Model_Lender_Base_Case_SAH.xlsx ¦ sheet:Assumptions | Reconcile and confirm the governing value; update the lower-ranked documents/model. | Y |
| F-005 | Info | P90/P50 = 93.55% with combined uncertainty 5.033% (recomputed). | calc:C009 | Compare with the independent yield report. |  |

## 3.3 WS3 - PV and Balance of Plant Engineering

| ID | Sev. | Finding | Evidence | Recommendation | CP |
| --- | --- | --- | --- | --- | --- |
| F-068 | High | PV DC capacity (kWp): documents disagree - values [148442.9, 150002.0] (spread 1.039%). | 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1; 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1; 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1 (part 2); 05_Design/Design_Basis_Report_SAH.pdf ¦ p.1 | Reconcile and confirm the governing value; update the lower-ranked documents/model. | Y |
| F-001 | Medium | Layout is indicative: no surveyed site boundary was supplied. | calc:C001 | Supply surveyed boundary and constraint layers. |  |
| F-002 | Medium | With 2 x 90 MVA transformers, N-1 loading at peak export is 152.0% (>100%): loss of one unit constrains export. | calc:C007 | Confirm N-1 philosophy with TSO or add transformer capacity / curtailment scheme. |  |
| F-012 | Medium | Document indicates an open/absent item: "MISSING (planned Q1 2027) BESS VS-5000 ¦" | 06_Equipment/Certificates_Register.xlsx ¦ sheet:Certificates | Confirm with the project team; request the missing evidence or close-out. |  |
| F-013 | Medium | Document indicates an open/absent item: "In progress Transformer 90 MVA ¦" | 06_Equipment/Certificates_Register.xlsx ¦ sheet:Certificates | Confirm with the project team; request the missing evidence or close-out. |  |
| F-015 | Medium | Document indicates an open/absent item: "No pile testing was performed in Blocks C and D; a supplementary programme (min." | 04_Technical_Studies/Geotechnical_Investigation_Report_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-019 | Medium | Document indicates an open/absent item: "PFAS: supplier declarations pending for BESS; PV modules declared PFAS-free backsheet (glass-glass)." | 09_Environmental_Social/ESIA_Summary_and_Biodiversity_Baseline_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-020 | Medium | Document indicates an open/absent item: "Lease signed, registration pending (2 plots) Block D (part) ¦" | 01_Corporate_Legal/Land_Lease_and_Easements_Summary_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. |  |
| F-021 | Medium | Document indicates an open/absent item: "<b>Option agreement not yet exercised; no signed lease/easement</b>" | 01_Corporate_Legal/Land_Lease_and_Easements_Summary_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. |  |
| F-022 | Medium | Document indicates an open/absent item: "A desk-study by a specialist UXO consultant has not been commissioned." | 04_Technical_Studies/UXO_Screening_Note_SAH.pdf ¦ p.1 | Confirm with the project team; request the missing evidence or close-out. |  |
| F-023 | Medium | Document indicates an open/absent item: "Grid-forming functionality: not included in the current scope." | 05_Design/Design_Basis_Report_SAH.pdf ¦ p.2 | Confirm with the project team; request the missing evidence or close-out. |  |

## 3.7 WS7 - BESS Technical Specialization

| ID | Sev. | Finding | Evidence | Recommendation | CP |
| --- | --- | --- | --- | --- | --- |
| F-026 | Medium | Document indicates an open/absent item: "98.0% of container hours (excludes grid, ambient >45 C, owner-caused events) Augmentation ¦" | 07_Contracts/BESS_Supply_and_LTSA_Key_Terms_SAH.docx ¦ table 1 | Confirm with the project team; request the missing evidence or close-out. |  |
| F-070 | Medium | BESS cycles per day: documents disagree - values [1.0, 1.2, 1.4] (spread 28.571%). | 07_Contracts/BESS_Supply_and_LTSA_Key_Terms_SAH.docx ¦ table 1; 10_Financial/Financial_Model_Lender_Base_Case_SAH.xlsx ¦ sheet:Assumptions; 10_Financial/Merchant_Price_Study_Iberia_SAH.pdf ¦ p.1 (part 2) | Reconcile and confirm the governing value; update the lower-ranked documents/model. |  |

## 3.4 WS4 - Grid, Controls and Digital Systems

| ID | Sev. | Finding | Evidence | Recommendation | CP |
| --- | --- | --- | --- | --- | --- |
| F-030 | Medium | Document indicates an open/absent item: "Open items EMT model validation for the selected PCS has not yet been submitted." | 08_Grid/Grid_Connection_Study_and_TSO_Letter_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-031 | Medium | Document indicates an open/absent item: "Grid-code compliance study (including GFM) not yet issued." | 08_Grid/Grid_Connection_Study_and_TSO_Letter_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-035 | Medium | Document indicates an open/absent item: "No IEC 62443 risk assessment or security-level target has been completed; no OEM IEC 62443-4-1/4-2 conformity certificates provided; no formal incident response plan or penetration test." | 12_Operations_Planning/OT_Cybersecurity_Overview_SAH.pdf ¦ p.1 | Confirm with the project team; request the missing evidence or close-out. |  |
| F-036 | Medium | Document indicates an open/absent item: "EU NIS2/Cyber Resilience Act applicability review pending." | 12_Operations_Planning/OT_Cybersecurity_Overview_SAH.pdf ¦ p.1 | Confirm with the project team; request the missing evidence or close-out. |  |
| F-003 | Info | PV (120.0 MWac) + BESS (60 MW) exceeds the 130 MW export limit; PPC export limiting is required. | calc:C007 | Quantify curtailment and BESS co-optimisation in the yield/revenue model. |  |

## 3.5 WS5 - Delivery and Operations

| ID | Sev. | Finding | Evidence | Recommendation | CP |
| --- | --- | --- | --- | --- | --- |
| F-041 | Medium | Document indicates an open/absent item: "BESS: capacity and RTE tests per EPC test procedure; <b>grid-forming tests: not applicable</b>." | 07_Contracts/EPC_Agreement_Key_Terms_and_Schedules_SAH.docx ¦ body (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-044 | Medium | Document indicates an open/absent item: "BESS safety design Container-level fire detection (smoke, heat, off-gas), aerosol suppression, explosion venting per NFPA 68/69 approach, 3 m separation between containers (to be confirmed by fire-spr" | 05_Design/Design_Basis_Report_SAH.pdf ¦ p.1 (part 3) | Confirm with the project team; request the missing evidence or close-out. |  |

## 3.6 WS6 - Commercial and Specialist Assurance

| ID | Sev. | Finding | Evidence | Recommendation | CP |
| --- | --- | --- | --- | --- | --- |
| F-004 | High | Minimum DSCR 0.514 is below the 1.30x sizing criterion at P50 inputs. | calc:C010 | Resize debt or revisit revenue assumptions. | Y |
| F-047 | Medium | Document indicates an open/absent item: "ework) Medium Traceability audit pending for upstream polysilicon Warranty backing Medium Parent company guarantee limited to 10 years 2." | 06_Equipment/Bankability_Report_Helion_PV_Modules.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |
| F-053 | Medium | Document indicates an open/absent item: "P90 and BESS sensitivities not included in lender model package ¦" | 10_Financial/Financial_Model_Lender_Base_Case_SAH.xlsx ¦ sheet:Sensitivities | Confirm with the project team; request the missing evidence or close-out. |  |
| F-054 | Medium | Document indicates an open/absent item: "Cost item (EUR m, today's prices) Gross PV dismantling & logistics 3.6 BESS removal & recycling 2.1 Substation, cabling, civil removal 1.7 Site restoration & monitoring 1.0 Total gross cost 8.4 Estima" | 13_Decommissioning/Decommissioning_Plan_SAH.pdf ¦ p.1 | Confirm with the project team; request the missing evidence or close-out. |  |
| F-055 | Medium | Document indicates an open/absent item: "cycling credits) (3.1) Net cost 5.3 Financial security: not defined." | 13_Decommissioning/Decommissioning_Plan_SAH.pdf ¦ p.1 (part 2) | Confirm with the project team; request the missing evidence or close-out. |  |

## 3.8 WS8 - Independent Assurance and Reporting

No findings.

# 4. Conditions precedent (proposed)

| Ref | Condition | Evidence |
| --- | --- | --- |
| F-004 | Resize debt or revisit revenue assumptions. | calc:C010 |
| F-068 | Reconcile and confirm the governing value; update the lower-ranked documents/model. | 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1; 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1; 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.1 (part 2); 05_Design/Design_Basis_Report_SAH.pdf ¦ p.1 |
| F-069 | Reconcile and confirm the governing value; update the lower-ranked documents/model. | 04_Technical_Studies/Energy_Yield_Assessment_Report_SAH.pdf ¦ p.2; 06_Equipment/Module_Datasheet_Helion_HX580BF.pdf ¦ p.1; 07_Contracts/Module_Supply_Agreement_Key_Terms_SAH.docx ¦ body; 10_Financial/Financial_Model_Lender_Base_Case_SAH.xlsx ¦ sheet:Assumptions |

# 5. QA verification

pass 10 / warn 0 / fail 0.

| Check | Agent | Status | Detail |
| --- | --- | --- | --- |

## Approval record

| Gate | Role | Decision | Actor | Date | Comment |
| --- | --- | --- | --- | --- | --- |
| engineering_review | Engineering Reviewer | PENDING |  |  |  |
| lead_approval | Lead Engineer | PENDING |  |  |  |
| director_approval | Project Director | PENDING |  |  |  |
| lender_engineer | Lender Engineer | PENDING |  |  |  |